HOLMSTONE

Energy Simple and Transparent

# Utility Recovery & Meter Accuracy Review

All Sites - Consumption-per-Day and Under/Over-Recovery Analysis

Prepared: August 2026

## Purpose

- This report explains, site by site, WHY each utility account is currently over- or under-recovered - focused on two things: how consumption-per-day compares between our own billed meter reading and the real municipal statement, and whether either meter appears to be within reasonable accuracy tolerance.

- Property Rates, Refuse and Sundry are excluded throughout - these are real municipal-only costs that are never billed through to the client, so including them would always show a large "under-recovery" that has nothing to do with utility metering accuracy.

## Method

- "Our Avg/Day" = our own billed reading for that month, divided by our own billing period length in days.

- "Municipal Avg/Day" = the real Ekurhuleni/City Power statement reading for the best-overlapping period, divided by that statement's own reading-period length in days - normalising both sides removes distortion from periods of different lengths (e.g. a combined 61-day statement).

- "Variance" = (Our Avg/Day - Municipal Avg/Day) / Municipal Avg/Day. Colour key used throughout every table in this report:

  - within 10% - normal, expected day-to-day/reading noise.

  - 10% to 25% - worth watching, not yet a red flag.

  - 25% or more - flagged for follow-up (either a real usage event, or a likely estimated/placeholder municipal read).

- "CoV" (coefficient of variation) measures how much a meter's own daily reading moves around from month to month. A LOW CoV means a steady, consistent reading; a HIGH CoV means an erratic one. Comparing our CoV against the municipal CoV is often more revealing than any single month's variance - a meter that is consistently steady while the other side swings wildly points to an estimate/read problem on the volatile side, not a real change in usage.

# Portfolio Summary

Net Electricity + Water + Sewer recovery per site, all overlapping months of data. Detail for each site follows on its own page.

| Site | Net Recovery (Excl VAT) | Data Window |
| --- | --- | --- |
| 8 Field Street | +R158,491 | Sep 25 - Jun 26 (10 months of overlapping data) |
| Bob Martin | -R67,494 | Dec 25 - Jun 26 (7 months of overlapping data) |
| Loper Road - Sandvic | -R12,114 | Dec 25 - Jun 26 (6 months of overlapping data) |
| AutoZone | -R168,366 | Dec 25 - Jun 26 (6 months of overlapping data) |
| Cranbrook Flavours | -R38,117 | Nov 25 - Jun 26 (4 months of overlapping data) |
| Wingfield Business Park | +R1,170,646 | Jun 25 - Jun 26 (13 months of overlapping data) |
| City Deep Industrial Park - Industrial Park (Industrial A & B accounts) | +R622,037 | Sep 25 - Jun 26 (10 months of overlapping data) |
| City Deep Industrial Park - City Deep (Rittle account) | -R366,706 | Sep 25 - Jun 26 (10 months of overlapping data) |
| City Deep Industrial Park - Mini Park (Mini account) | +R578,313 | Sep 25 - Jun 26 (10 months of overlapping data) |

# 8 Field Street

Sep 25 - Jun 26 (10 months of overlapping data)

## Recovery Summary

| Utility | Net Recovery (Excl VAT) | Reading |
| --- | --- | --- |
| Electricity | +R166,404 | Over-recovered |
| Water | -R5,716 | Under-recovered |
| Sewer | -R2,196 | Under-recovered |
| TOTAL | +R158,491 | Net over-recovered |

## Why

- Electricity - meters agree closely: monthly variance never exceeds 3.2% in either direction, and our own day-to-day usage volatility (10.5%) is almost identical to the municipal side (10.3%). The two meters are effectively tracking the same real consumption every month.

- Electricity result: +R166,404 over-recovered across 10 months - a small, consistent margin (not a metering issue), reflecting the agreed billing tariff sitting slightly above the municipal rate.

- Water/Sewer - noisy but immaterial: 5 of 10 months show a >25% variance, but this is a very low-volume account (4-7 kL/day), so small absolute differences read as large percentages. The municipal reading is far more volatile (53.9% CoV) than ours (17.2%) - e.g. October 2025 the municipal reading collapsed to just 0.27 kL/day, an implausible one-off, most likely an estimated read.

- Water/Sewer result: -R5,716 / -R2,196 under-recovered - both figures are small enough to be rounding/estimate noise on the municipal side rather than a genuine loss.

## Meter Accuracy - Average Daily Usage (kL)

| Month | Our Avg/Day | Municipal Avg/Day | Variance |
| --- | --- | --- | --- |
| Jul 25 | no overlapping data |  |  |
| Aug 25 | no overlapping data |  |  |
| Sep 25 | 6.87 kL/day | 13.50 kL/day | -49.1% |
| Oct 25 | 7.03 kL/day | 0.27 kL/day | +772.0% |
| Nov 25 | 4.07 kL/day | 6.83 kL/day | -40.5% |
| Dec 25 | 5.42 kL/day | 4.46 kL/day | +34.4% |
| Jan 26 | 5.00 kL/day | 5.73 kL/day | -18.0% |
| Feb 26 | 4.93 kL/day | 7.68 kL/day | -35.8% |
| Mar 26 | 6.15 kL/day | 5.74 kL/day | +7.1% |
| Apr 26 | 7.26 kL/day | 2.90 kL/day | +19.0% |
| May 26 | 6.91 kL/day | 6.73 kL/day | -3.4% |
| Jun 26 | 6.43 kL/day | 6.43 kL/day | 0.0% |
| Jul 26 | no overlapping data |  |  |

# Bob Martin

Dec 25 - Jun 26 (7 months of overlapping data)

## Recovery Summary

| Utility | Net Recovery (Excl VAT) | Reading |
| --- | --- | --- |
| Electricity | -R26,991 | Under-recovered |
| Water | -R29,271 | Under-recovered |
| Sewer | -R11,233 | Under-recovered |
| TOTAL | -R67,494 | Net under-recovered |

## Why

- Electricity - balanced, tiny consistent gap: variance sits at a steady ~-1% every single month, and both sides move together in lockstep (our CoV and municipal CoV are identical at 30.4%). This is a stable pricing/rounding difference, not an accuracy problem.

- Electricity result: -R26,991 under-recovered across 7 months - immaterial relative to the ~R3,300/month average bill.

- Water/Sewer - this is a billing gap, not a meter issue: our own billing shows R0 (0 kL) in 6 of the 7 overlapping months, while Ekurhuleni charged real water/sewer every month without exception. The one month it was billed (May 2026), our reading (3.45 kL/day) matched the municipal reading (3.82 kL/day) almost exactly - proving the metering itself is fine when we actually invoice it.

- Water/Sewer result: -R29,271 / -R11,233 under-recovered - this is recoverable by simply invoicing water/sewer every month going forward, not a dispute with the municipality.

## Meter Accuracy - Average Daily Usage (kL)

| Month | Our Avg/Day | Municipal Avg/Day | Variance |
| --- | --- | --- | --- |
| Jul 25 | no overlapping data |  |  |
| Aug 25 | no overlapping data |  |  |
| Sep 25 | no overlapping data |  |  |
| Oct 25 | no overlapping data |  |  |
| Nov 25 | no overlapping data |  |  |
| Dec 25 | 0.00 kL/day | 4.03 kL/day | -100.0% |
| Jan 26 | 0.00 kL/day | 0.53 kL/day | -100.0% |
| Feb 26 | 0.00 kL/day | 3.75 kL/day | -100.0% |
| Mar 26 | 0.00 kL/day | 3.39 kL/day | -100.0% |
| Apr 26 | 0.00 kL/day | 1.16 kL/day | -100.0% |
| May 26 | 3.45 kL/day | 3.82 kL/day | 0.0% |
| Jun 26 | 0.00 kL/day | 3.68 kL/day | -100.0% |
| Jul 26 | no overlapping data |  |  |

# Loper Road - Sandvic

Dec 25 - Jun 26 (6 months of overlapping data)

## Recovery Summary

| Utility | Net Recovery (Excl VAT) | Reading |
| --- | --- | --- |
| Electricity | +R8,789 | Over-recovered |
| Water | -R15,097 | Under-recovered |
| Sewer | -R5,805 | Under-recovered |
| TOTAL | -R12,114 | Net under-recovered |

## Why

- Electricity - tight agreement: variance is within ~1.8% every month except April 2026 (-15.5%), which lines up with the known account-changeover statement that combined April and May consumption into one 61-day read (see the Municipal Account page notes) - a one-off, explainable event.

- Electricity result: +R8,789 over-recovered across 6 months - effectively break-even.

- Water/Sewer - same billing gap as Bob Martin: our billing shows 0 kL water in all 6 overlapping months, while Ekurhuleni billed real water/sewer at R49.11/kL and R18.91/kL throughout. There is no metering discrepancy to explain here - water/sewer simply is not being invoiced to this tenant yet.

- Water/Sewer result: -R15,097 / -R5,805 under-recovered - fully recoverable by adding water/sewer to this site's monthly invoice.

## Meter Accuracy - Average Daily Usage (kL)

| Month | Our Avg/Day | Municipal Avg/Day | Variance |
| --- | --- | --- | --- |
| Jul 25 | no overlapping data |  |  |
| Aug 25 | no overlapping data |  |  |
| Sep 25 | no overlapping data |  |  |
| Oct 25 | no overlapping data |  |  |
| Nov 25 | no overlapping data |  |  |
| Dec 25 | 0.00 kL/day | 1.72 kL/day | -100.0% |
| Jan 26 | 0.00 kL/day | 2.21 kL/day | -100.0% |
| Feb 26 | 0.00 kL/day | 1.93 kL/day | -100.0% |
| Mar 26 | 0.00 kL/day | 1.77 kL/day | -100.0% |
| Apr 26 | 0.00 kL/day | 0.61 kL/day | -100.0% |
| May 26 | no overlapping data |  |  |
| Jun 26 | 0.00 kL/day | 1.23 kL/day | -100.0% |
| Jul 26 | no overlapping data |  |  |

# AutoZone

Dec 25 - Jun 26 (6 months of overlapping data)

## Recovery Summary

| Utility | Net Recovery (Excl VAT) | Reading |
| --- | --- | --- |
| Electricity | +R297,876 | Over-recovered |
| Water | -R268,949 | Under-recovered |
| Sewer | -R197,293 | Under-recovered |
| TOTAL | -R168,366 | Net under-recovered |

## Why

- Electricity - solid, no red flags: variance stays within 15% across all overlapping months; +R297,876 over-recovered across 6 months.

- Water - the standout finding on the whole portfolio: our own meter is remarkably constant at ~25 kL/day, every single month (CoV just 0.9%) - exactly what you would expect from a stable retail operation with no seasonal swing. The municipal reading, by contrast, is wildly erratic (CoV 81%): 11 kL/day in April 2026, 51 kL/day in May, then 113 kL/day in June - a swing of more than 10x on an account whose real usage plainly has not moved.

- Interpretation: a flat line on our side against a sawtooth on the municipal side is the signature of Ekurhuleni estimating this meter for several months and then "catching up" with a correction read - not evidence that AutoZone's real consumption changed. This should be raised directly with Ekurhuleni as a formal query, using our own steady sub-metered readings as the supporting evidence.

- Water result: -R268,949 under-recovered across 6 months - by far the largest single utility exposure in the portfolio, and one where the data supports disputing the municipal readings rather than accepting them as ground truth.

## Meter Accuracy - Average Daily Usage (kL)

| Month | Our Avg/Day | Municipal Avg/Day | Variance |
| --- | --- | --- | --- |
| Jul 25 | no overlapping data |  |  |
| Aug 25 | no overlapping data |  |  |
| Sep 25 | no overlapping data |  |  |
| Oct 25 | no overlapping data |  |  |
| Nov 25 | no overlapping data |  |  |
| Dec 25 | 25.32 kL/day | 28.64 kL/day | +24.6% |
| Jan 26 | 24.61 kL/day | 28.32 kL/day | -29.1% |
| Feb 26 | no overlapping data |  |  |
| Mar 26 | 24.81 kL/day | 20.15 kL/day | -36.4% |
| Apr 26 | 25.00 kL/day | 10.97 kL/day | +128.0% |
| May 26 | 25.05 kL/day | 51.00 kL/day | -62.9% |
| Jun 26 | 25.18 kL/day | 113.13 kL/day | -77.7% |
| Jul 26 | no overlapping data |  |  |

# Cranbrook Flavours

Nov 25 - Jun 26 (4 months of overlapping data)

## Recovery Summary

| Utility | Net Recovery (Excl VAT) | Reading |
| --- | --- | --- |
| Electricity | +R15,755 | Over-recovered |
| Water | -R38,877 | Under-recovered |
| Sewer | -R14,996 | Under-recovered |
| TOTAL | -R38,117 | Net under-recovered |

## Why

- Data caveat: only 3-4 months of overlapping billing/municipal data are available so far - treat the conclusions below as preliminary until more months land.

- Electricity - erratic municipal readings: November 2025 shows a +416% variance (the municipal statement recorded only ~30 kWh for the whole month against our metered ~155 kWh/day - clearly a placeholder/estimated read), while May and June 2026 run the other way, with municipal readings ~40% above ours.

- Electricity result: +R15,755 over-recovered across the available months.

- Water/Sewer - same billing-gap pattern as Bob Martin/Loper Road: our own billing shows 0 kL every month while Ekurhuleni billed real water/sewer consumption throughout.

- Water/Sewer result: -R38,877 / -R14,996 under-recovered - recoverable by invoicing water/sewer, pending confirmation once more months of data are available.

## Meter Accuracy - Average Daily Usage (kL)

| Month | Our Avg/Day | Municipal Avg/Day | Variance |
| --- | --- | --- | --- |
| Jul 25 | no overlapping data |  |  |
| Aug 25 | no overlapping data |  |  |
| Sep 25 | no overlapping data |  |  |
| Oct 25 | no overlapping data |  |  |
| Nov 25 | 0.00 kL/day | 0.00 kL/day | - |
| Dec 25 | no overlapping data |  |  |
| Jan 26 | no overlapping data |  |  |
| Feb 26 | no overlapping data |  |  |
| Mar 26 | 0.00 kL/day | 4.80 kL/day | -100.0% |
| Apr 26 | no overlapping data |  |  |
| May 26 | 0.00 kL/day | 7.64 kL/day | -100.0% |
| Jun 26 | 0.00 kL/day | 7.97 kL/day | -100.0% |
| Jul 26 | no overlapping data |  |  |

# Wingfield Business Park

Jun 25 - Jun 26 (13 months of overlapping data)

## Recovery Summary

| Utility | Net Recovery (Excl VAT) | Reading |
| --- | --- | --- |
| Electricity | +R1,786,322 | Over-recovered |
| Water | -R447,261 | Under-recovered |
| Sewer | -R168,415 | Under-recovered |
| TOTAL | +R1,170,646 | Net over-recovered |

## Why

- Electricity - reasonable agreement: only 1 of 13 months is flagged (Feb 2026, +37.4%); the Rand gap is a tariff/pricing-structure story rather than a volume-accuracy one, since daily kWh usage tracks closely on both sides.

- Electricity result: +R1,786,322 over-recovered across 13 months - reflects the billed tariff margin, not a meter mismatch.

- Water/Sewer - a genuine, structural gap: every single month (13 of 13) is flagged, with a consistent negative bias of roughly -30% to -70% - our billed volume is routinely half or less of what the municipal bulk meter measures. Because this pattern repeats every month rather than appearing as random noise, it points to unmetered or unsub-metered water use (common areas, irrigation, fire systems) that the bulk meter captures but tenant-level billing does not.

- Recommendation: a physical walk-through/audit of Wingfield's water reticulation to identify what the bulk meter is picking up that isn't currently sub-metered to tenants.

- Water/Sewer result: -R447,261 / -R168,415 under-recovered - the largest recurring exposure in the portfolio, and one that needs a site audit rather than a billing fix.

## Meter Accuracy - Average Daily Usage (kL)

| Month | Our Avg/Day | Municipal Avg/Day | Variance |
| --- | --- | --- | --- |
| Jun 25 | 17.99 kL/day | 33.36 kL/day | -49.4% |
| Jul 25 | 26.82 kL/day | 39.17 kL/day | -41.0% |
| Aug 25 | 17.10 kL/day | 32.11 kL/day | -52.8% |
| Sep 25 | 17.83 kL/day | 33.75 kL/day | -31.8% |
| Oct 25 | 23.84 kL/day | 37.97 kL/day | -46.2% |
| Nov 25 | 18.93 kL/day | 35.76 kL/day | -50.3% |
| Dec 25 | 20.94 kL/day | 33.85 kL/day | -28.6% |
| Jan 26 | 14.51 kL/day | 50.50 kL/day | -65.5% |
| Feb 26 | 20.68 kL/day | 44.50 kL/day | -57.6% |
| Mar 26 | 19.34 kL/day | 68.10 kL/day | -69.7% |
| Apr 26 | 18.14 kL/day | 46.47 kL/day | -65.6% |
| May 26 | 26.81 kL/day | 50.68 kL/day | -55.6% |
| Jun 26 | 21.12 kL/day | 52.37 kL/day | -59.7% |
| Jul 26 | no overlapping data |  |  |

# City Deep Industrial Park

Industrial Park (Industrial A & B accounts)

Sep 25 - Jun 26 (10 months of overlapping data)

## Recovery Summary

| Utility | Net Recovery (Excl VAT) | Reading |
| --- | --- | --- |
| Electricity | +R1,909,834 | Over-recovered |
| Water | -R1,540,123 | Under-recovered |
| Sewer | +R252,327 | Over-recovered |
| TOTAL | +R622,037 | Net over-recovered |

## Why

- Electricity - erratic municipal readings, not a fault on our side: 9 of 10 months are flagged; the municipal side is highly volatile (CoV 52.4%) against our steady, consistent billing (CoV 16.8%). Several municipal readings are implausibly low for two large industrial accounts combined - November 2025 averaged just 580 kWh/day, June 2026 only 232 kWh/day - consistent with estimated/placeholder municipal reads that get corrected later.

- Electricity result: +R1,909,834 over-recovered across 10 months - this reflects real consumption we are billing correctly against municipal statements that understate usage in most months, not an over-billing risk.

- Water/Sewer - same underlying volume noise, split Rand outcome: water and sewer share the identical consumption reading (same meter, different tariff), so both utilities show the same erratic variance pattern month to month. The Rand outcome diverges purely because of the different tariff rates applied - Water: -R1,540,123 under-recovered; Sewer: +R252,327 over-recovered.

## Meter Accuracy - Average Daily Usage (kWh)

| Month | Our Avg/Day | Municipal Avg/Day | Variance |
| --- | --- | --- | --- |
| Jul 25 | no overlapping data |  |  |
| Aug 25 | no overlapping data |  |  |
| Sep 25 | 13912.44 kWh/day | 4853.24 kWh/day | +286.4% |
| Oct 25 | 13980.56 kWh/day | 5007.37 kWh/day | +52.8% |
| Nov 25 | 14591.71 kWh/day | 579.80 kWh/day | +139.7% |
| Dec 25 | 15653.39 kWh/day | 7720.33 kWh/day | +23.9% |
| Jan 26 | 8627.89 kWh/day | 5983.18 kWh/day | +55.9% |
| Feb 26 | 11808.79 kWh/day | 9107.35 kWh/day | +44.1% |
| Mar 26 | 10822.20 kWh/day | 7651.03 kWh/day | +32.0% |
| Apr 26 | 11072.55 kWh/day | 9032.03 kWh/day | +26.8% |
| May 26 | 11092.22 kWh/day | 7600.30 kWh/day | +50.8% |
| Jun 26 | 10968.79 kWh/day | 232.49 kWh/day | +4618.0% |
| Jul 26 | no overlapping data |  |  |

# City Deep Industrial Park

City Deep (Rittle account)

Sep 25 - Jun 26 (10 months of overlapping data)

## Recovery Summary

| Utility | Net Recovery (Excl VAT) | Reading |
| --- | --- | --- |
| Electricity | -R310,444 | Under-recovered |
| Water | -R29,292 | Under-recovered |
| Sewer | -R26,971 | Under-recovered |
| TOTAL | -R366,706 | Net under-recovered |

## Why

- Electricity - the key finding on this account: 7 of 10 months are flagged, with the municipal side highly erratic (CoV 69.4%) against our steady billing (CoV 14.7%). The underlying cause is visible in Ekurhuleni's own statement detail: reactive energy (kVARh) charges run 3-6x our active kWh reading in almost every month (see table below), while the demand charge is billed at a flat 70 kVA in effectively every one of the 10 months regardless of actual load - a classic signature of an estimated, not measured, demand/reactive reading being carried forward month after month.

- The correction: in June 2026 the reactive reading suddenly collapsed to 7,350 kVARh (in line with real load for the first time all year) - consistent with a genuine meter read finally landing that month after many months of estimates.

- Electricity result: -R310,444 under-recovered across 10 months. Because our own billing is based on measured kWh only and does not carry Ekurhuleni's reactive-energy estimate swings, this under-recovery is a tariff-structure/estimate issue on the municipal side, not a fault in our own metering - worth raising directly with Ekurhuleni, supported by the pattern below.

- Water/Sewer: -R29,292 / -R26,971 under-recovered - smaller, with moderate volatility on both sides (municipal CoV 29.2%, ours 30.0%) and no single dominant driver.

## Meter Accuracy - Average Daily Usage (kWh)

| Month | Our Avg/Day | Municipal Avg/Day | Variance |
| --- | --- | --- | --- |
| Jul 25 | no overlapping data |  |  |
| Aug 25 | no overlapping data |  |  |
| Sep 25 | 490.58 kWh/day | 303.48 kWh/day | +72.8% |
| Oct 25 | 487.17 kWh/day | 313.54 kWh/day | -23.6% |
| Nov 25 | 514.50 kWh/day | 329.41 kWh/day | +56.2% |
| Dec 25 | 574.18 kWh/day | 334.05 kWh/day | +26.0% |
| Jan 26 | 667.40 kWh/day | 531.41 kWh/day | +67.5% |
| Feb 26 | 750.67 kWh/day | 546.64 kWh/day | +52.6% |
| Mar 26 | 607.71 kWh/day | 633.20 kWh/day | -7.3% |
| Apr 26 | 582.40 kWh/day | 1777.99 kWh/day | -67.2% |
| May 26 | 516.39 kWh/day | 547.87 kWh/day | -2.6% |
| Jun 26 | 486.90 kWh/day | 653.07 kWh/day | -25.4% |
| Jul 26 | no overlapping data |  |  |

## Ekurhuleni Statement Detail - Active vs Reactive Energy

Reactive energy (kVARh) and demand (kVA) readings pulled directly from each month's Ekurhuleni statement - not part of the standard Recovery comparison above, shown here because it explains the pattern.

| Month | Active kWh | Reactive kVARh | Reactive/Active | Demand kVA Billed |
| --- | --- | --- | --- | --- |
| Sep 25 | 8,801 | 45,030 | 5.12x | 70.0 |
| Oct 25 | 9,698 | 49,622 | 5.12x | 70.0 |
| Nov 25 | 10,541 | 59,546 | 5.65x | 70.0 |
| Dec 25 | 10,022 | 49,788 | 4.97x | 70.0 |
| Jan 26 | 15,942 | 64,685 | 4.06x | 70.0 |
| Feb 26 | 14,759 | 59,886 | 4.06x | 70.0 |
| Mar 26 | 18,363 | 68,119 | 3.71x | 70.0 |
| Apr 26 | 53,340 | 82,864 | 1.55x | 70.0 |
| May 26 | 16,436 | 97,882 | 5.96x | 70.0 |
| Jun 26 | 18,939 | 7,350 | 0.39x | 70.0 |

# City Deep Industrial Park

Mini Park (Mini account)

Sep 25 - Jun 26 (10 months of overlapping data)

## Recovery Summary

| Utility | Net Recovery (Excl VAT) | Reading |
| --- | --- | --- |
| Electricity | +R477,690 | Over-recovered |
| Water | +R50,123 | Over-recovered |
| Sewer | +R50,500 | Over-recovered |
| TOTAL | +R578,313 | Net over-recovered |

## Why

- Electricity - the most balanced account in the portfolio: only 4 of 10 months are flagged, and municipal volatility (CoV 30.6%) is moderate rather than extreme. January 2026 is the outlier (+89.8%), where the municipal reading dropped sharply for that one month only.

- Electricity result: +R477,690 over-recovered across 10 months - a healthy, explainable margin.

- Water/Sewer - one of the few utilities in slight over-recovery: both sides move together closely (municipal CoV 31.1% vs ours 25.5%); January 2026 is again the outlier (+311%, again a low municipal reading that month).

- Water/Sewer result: +R50,123 / +R50,500 over-recovered - this account requires no corrective action.

## Meter Accuracy - Average Daily Usage (kWh)

| Month | Our Avg/Day | Municipal Avg/Day | Variance |
| --- | --- | --- | --- |
| Jul 25 | no overlapping data |  |  |
| Aug 25 | no overlapping data |  |  |
| Sep 25 | 2924.36 kWh/day | 2998.52 kWh/day | +31.4% |
| Oct 25 | 2148.02 kWh/day | 1717.03 kWh/day | +25.1% |
| Nov 25 | 2718.39 kWh/day | 2238.31 kWh/day | +21.4% |
| Dec 25 | 2113.28 kWh/day | 1909.41 kWh/day | -9.8% |
| Jan 26 | 1668.49 kWh/day | 950.19 kWh/day | +89.8% |
| Feb 26 | 2657.25 kWh/day | 2242.52 kWh/day | +31.7% |
| Mar 26 | 2610.35 kWh/day | 2041.47 kWh/day | +19.3% |
| Apr 26 | 2559.01 kWh/day | 2435.52 kWh/day | +8.7% |
| May 26 | 2680.57 kWh/day | 2426.50 kWh/day | +14.2% |
| Jun 26 | 3215.92 kWh/day | 3679.24 kWh/day | -12.6% |
| Jul 26 | no overlapping data |  |  |